## Sheet1
Solar Powered Repeater Battery and Solar Array Sizing by Jeff Liebermann v2.07
Repeater Call Sign | WR6AOK
Date | 2026-07-28
Repeater | Current Drain | Duty cycle | A-hr/day |  | Summary
Xmitter | 20 | 8 | 38.4 |  | Daily Drain | 1029.6 | watt-hrs/day
Receiver | 1.5 | 100 | 36 |  | Daily Solar charge | 1080 | watt-hrs/day
Controller | 0.2 | 100 | 4.8 |  | Runtime w/o charge | 0.8286 | days
Link receiver | 0 | 100 | 0 |  | Days to recharge | 0.95333 | days with no load
Other 1 | 0 | 100 | 0 |  | Days to recharge | 21.4286 | days with full load
Other 2 | 0 | 100 | 0
Target value is one day to recharge without a load.
Total drain | 79.2 | A-Hrs/day |  |  | If the days to recharge with a full load is negative,
Voltage | 13 | Volts |  |  | where the daily charge does not exceed the daily drain,
Power drain | 1029.6 | watt-hrs/day |  |  | then the batteries will never charge. A better target
would be to recharge in one day with a full load.
Battery
Battery Capacity @ 25C | 375 | Amp-hrs |  | Room temperature capacity.
Operating Temperature | 60 | F |  | Battery temp, not ambient temp.
Battery Deration | 0.875 |  |  | 50% capacity at 0F
Discharge point | 80 | % of capacity |  | 20% discharge is considered safe.
Available capacity | 65.625 | Amp-hrs |  | How much can be drained from battery.
Voltage | 13 | Volts
Delivered power | 853.125 | watt-hrs |  | Available capacity in A-hrs * Volts
Runtime without charge | 19.8864 | hours
Runtime without charge | 0.8286 | days
Solar Array |  |  |  | NREL Flat Plate Solar Collector Calcs
Rated solar array capacity | 400 | watts |  | Adjust size of array until Days to recharge equals one.
Winter Insolation | 3 | equiv hours/day |  | Flat plate, non-tracking array. Mid-Winter. Kw-hr/m^2/day
Tracking factor | 1 |  |  | Non-Tracking = 1.0 Tracking = 1.3
Delivered power | 1200 | watt-hrs/day
Battery charge efficiency | 90 | % |  | Varies with controller.
Solar Charge | 1080 | watt-hrs/day